## BMS Sen Specs
Specification for BMS Sensors/Controllers
Current flow sensors | Transmission rate: reports average = 5 measurements every 30 seconds Measurement ranges: 1. 1A-60A (+/- 0.1A or 2%, whichever is greater) 2. 2A-200A (+/- 0.1A or 2.5%, whichever is greater) 3. 2A-600A (+/- 0.1A or 3%, whichever is greater) 4. AC current frequencies: 60Hz Power specification Power: energy harvesting Wireless specification Radio frequency: Range 30 - 300 meters Protocol:- EnOcean EnOcean Equipment Profile (EEP): D2-32-02 Interoperability: EnOcean certification 2.0 IP rating: IP4X minimum Fixing: clamp clips around single core cable. Operating temperature and humidity range: -5°C to +40°C; 0-85% Storage temperature and humidity range: -20°C to +55°C; 0-85% Environment: indoor/outdoor CE approved, RoHS compliant, FCC compliant
Temp Sensors | Measurement Transmission rate: every 30 seconds (with configurable Rates) Measurement range: -20 to 100ºC ½ºC steps (accuracy +/- 1°C) Power specification Power: battery Battery life: up to 10 years Wireless specification Protocol: EnOcean Range: up to 30 - 300 metres EnOcean Equipment compatibility Security: mode AES-128 encryption Minimum Interoperability: EnOcean certification 3.0 Enclosure specification IP rating: IP65 Temperature: -20ºC to +55ºC Calibration: State calibration requirements (When and Fequency) Compliance: CE approved, RoHS compliant, FCC compliant Voltage: 0 to 24 volts DC
Air Quality Sensors | Transmission rate: reports every 5-60 seconds Measurement range: 0 to 60000 ppb Resolution: 1 - 32 ppb Power specification: DC Wireless specification Protocol: EnOcean/wireless Range: up to 30 - 300 metres Ocean Equipment Profile (EEP) Ocean Equipment Profile Security: 128 AES encryption configurable IP rating: IP2X Operating temperature range: -10oC to +55oC Environment: indoor Calibration: State calibration requirements (When and Frequency) Compliance: - CE approved, RoHS compliant, WEE directive compliant, FCC compliant Voltade: 0 to 24 volts DC
CO2 Sensor | Transmission rate: reports every 5 minutes when powered by solar and 15 minutes when powered by battery Measurement range: CO2 0-2550PPM (accuracy +/- 125PPM) Temperature 0-51ºC (accuracy +/- 0.5ºC) Humidity 0-100% RH (accuracy +/- 5%) Power specification Typical battery life: up to 10 years (dependent on ambient light conditions and use) Wireless specification: Protocol: EnOcean/wireless/Bluetooth 5.3 Range: up to 30 metres in buildings and 300 metres in free field Interoperability: EnOcean certification Wireless/Bluetooth 5.3 IP rating: IP2X Operating temperature: -5ºC to +55ºC Environment: indoor Calibration: State calibration requirement (When and Freuency) Compliamce:- CE approved, RoHS compliant, WEE directive compliant, FCC compliant Voltage:- 0 to 24 volts DC
Humidity Sensors | Measures relative Humidity Humidity:- 0-100% RH (+/- 5% between 30-70%) Reportings :- Humidity changes by more than 1 - 2%, End of life:- 10 years or better Communication:- Wireless EnOcean, wireless protocol, Bluetooth 5.3 Security: AES-128 encryption or higher Calibration: State calibration requirement (When and Freuency) Compliamce:- CE approved, RoHS compliant, WEE directive compliant, FCC compliant Voltage:- 0 to 24 volts DC
Air Quality/Temp/ Humidity Sensors | Measures temperature and relative humidity: Temperature 0-40ºC (+/- 0.5ºC between 17-27°C otherwise +/- 1°C) Humidity 0-100% RH (+/- 5% between 30-70%) Reports if the temperature changes by more than 0.5°C or humidity changes by more than 2%, End of life:- 10 years or longer Communication:- Wireless EnOcean, wireless protocol, Bluetooth 5.3 Security: AES-128 encryption or higher Calibration: State calibration requirement (When and Freuency) Compliamce:- CE approved, RoHS compliant, WEE directive compliant, FCC compliant Voltage:- 0 to 24 volts DC
CO₂, temperature and humidity sensor | Measurement range CO₂ 0-2550 PPM Temperature 0ºC to +51ºC Humidity 0-100% RH Accuracy CO₂ +/- 125 PPM Temperature +/- 0.5ºC Humidity +/- 5% for RH Sampling rate: 2 to 15 minutes, Environment:- IP2X Operating temperature & humidity range -5ºC to +60ºC Storage temperature & humidity range -20ºC to +55ºC Sensor response time:- transmission within two seconds of measurement Reporting: if the temperature changes by more than 0.5°C or humidity changes by more than 1 - 2%, End of life:- 10 years or better Communication:- Wireless EnOcean, wireless protocol, Bluetooth 5.3 Security: AES-128 encryption or higher Calibration: State calibration requirement (When and Freuency) Compliamce:- CE approved, RoHS compliant, WEE directive compliant, FCC compliant Voltage:- 0 to 24 volts DC
Light Controls | Controller Specifications Wireless Switch Specifications Power supply type: 0 to 240 Volt AC or 0 to 24 volts DC Voltage Range:0 to 240 Volt AC or 0 to 24 volts DC Max Load for LED Lighting 5 - 100W Life Time: 150,000 times on/off or more Work Environment Temperature: -30° -50°C Control Distance: 30 to 300M Power Source: self-powered or by other low power source Comunication:EnOcean/Wireless/Bluetooth 5.3 Life Time: 200,000 times on/off or better Control Distance: 30m - 300m
Night Set backs | Specification: Communication: Wireless Technology: EnOcean/Wireless/Bluetooyh 5.3 Security: AES-128 encryption or higher Calibration: State calibration requirement (When and Freuency) Compliamce:- CE approved, RoHS compliant, WEE directive compliant, FCC compliant Voltage:- 0 to 24 volts DC Measurement PIR Detection Area: 110 - 150 ° Horizontal, 70 - 100 ° Vertical Detection Distance: Maximum 6 -10 m Light Status: Bright/Dark (Determine 1-60000 lux as Bright or Dark according to custom threshold) Software: Agnostic Operating Temperature: -20°C to +60°C Relative Humidity: ≤90% (non-condensing) Ingress Protection: IP30 Regulatory Standard: CE, FCC, RoHS
Water Flow and Control Sensors | Specification: Operating Temp class T50 (0.1 – 50 oC) Storage temperature Voltage: - 0 to 240 Volt AC or 0 to 24 volts DC Maximum admissible pressure (MPa):-1.6 - 40 Protection class IP Rating:- IP68 Environmental class E1, M1 Battery 10 years or longer if battery operated Wireless Communication:Bluetooth5.3 WAN Communication/Wireless Metrological LED:- 10 000 imp/m3 Security: AES-128 encryption or higher Calibration: State calibration requirement (When and Freuency) Compliamce:- CE approved, RoHS compliant, WEE directive compliant, FCC compliant Voltage:- 0 to 24 volts DC
Wireless leak Detection System | Specifications: Panel Power supply: 230Vac 60Hz (90 ~ 264Vac) Alarm Indicators Events log storage Monitored Inputs Maximum number 255 event or more Wireless devices:- EnOcean/Wireless/Bluetooth 5.3 Liquid crystal display with scrolling text for leak & fault location 255 events maximum System Agnostic
Solar Sensor | In progress
Fire Alarm Sensors | In progress
AC Control and Monitoring | Communication:- Wireless EnOcean, wireless protocol, Bluetooth 5.3 Security: AES-128 encryption or higher Calibration: State calibration requirement (When and Freuency) Compliamce:- CE approved, RoHS compliant, WEE directive compliant, FCC compliant Voltage:- 0 to 240volts AC or 0 to 24 volts DC Accuracy:- ±0.2 °C / ±0.36 °F Operationg Standards: Analog (4…20 mA) and Modbus RTU output options/System Agnostic Temperature Accuracy:- ±0.5°C or ±1℉ Set-Point Range:- 5 - 35°C Display Temp. Range : 5 - 99°C Timing Error:- < 1% IP Rating:- IP20 or better